## Site parameters
Site and plant parameters
Average water depth at site | 22.5 | m
Distance between port and site | 124 | km
Distance between cable landfall and offshore substation | 42 | km
Distance between cable landfall and cabling vessel anchor point | 0 | km
Distance between cable landfall and onshore interconnection point | 3 | km
Number of turbines | 50 | turbines
Spacing between turbines in a string | 7 | rotor diameters
Spacing between strings | 9 | rotor diameters
Distance from offshore substation to first turbine on each string | 1 | km
Total plant capacity | 400 | MW
Number of export cables | 2 | cables

## Project plan - turbine install
Times for individual turbine installation processes
*Assumes 4 turbine sets transported per trip
| Relations/predecessors [row] | Start time [hours] | End time [hours] | Duration [hr] | Wind speed limit (m/s) | Wave height limit (m) | Time per turbine |  |  | Time per trip |  |  | Total installation time (unweathered) | Total installation time; 1-hour time-step (unweathered)
Mobilize vessel |  | 0 | 120 | 120 | [8 empty] | 120 | 120 | assume 1 mobilisation for vessel
Time required to fasten 2 tower sections to the vessel | 5 | 120 | 128 | 8 | 25 | 3 m swh | Loadout time per turbine | 16.5 | hr | Total loadout time per trip | 66 | hr | 400 | 400 | assume all 50 turbines loaded-out
Time required to fasten the nacelle to the vessel | 6 | 128 | 132 | 4 | 25 | 3 m swh | [6 empty] | 200 | 200
Time required to fasten 3 blades to the vessel | 7 | 132 | 136.5 | 4.5 | 25 | 3 m swh | [6 empty] | 225 | 250
Transit to site | 8 | 136.5 | 141.5 | 5 | 25 |  |  |  |  | Transit time per trip | 5 | hr | 65 | 65 | assume 13 trips to site (12 trips * 4 turbines plus 1 trip * 2 turbines)
Time required to position vessel at site | 9 | 141.5 | 143.5 | 2 | 25 | 2 m swh | Install time per turbine | 53.25 | hr | Total install time per trip | 213 | hr | 100 | 100 | assume all 50 turbines are installed
Time for vessel to jackup | 10 | 143.5 | 144.85 | 1.35 | 25 | 2 m swh | [6 empty] | 67.5 | 50
Time required to release the a tower section from the vessel | 11 | 144.85 | 147.85 | 3 | 25 | 2 m swh | [6 empty] | 150 | 150
Time required to lift tower section | 12 | 147.85 | 148.85 | 1 | 15 | 2 m swh | [6 empty] | 50 | 50
Time required to attach the turbine tower to the transition piece | 13 | 148.85 | 154.85 | 6 | 15 | 2 m swh | [6 empty] | 300 | 300
Time required to release the a tower section from the vessel | 14 | 154.85 | 157.85 | 3 | 25 | 2 m swh | [6 empty] | 150 | 150
Time required to lift tower section | 15 | 157.85 | 158.85 | 1 | 15 | 2 m swh | [6 empty] | 50 | 50
Time required to attach the turbine tower to the transition piece | 16 | 158.85 | 164.85 | 6 | 15 | 2 m swh | [6 empty] | 300 | 300
Time required to re-equip crane | 17 | 164.85 | 165.85 | 1 | 25 | 2 m swh | [6 empty] | 50 | 50
Time required to release the nacelle from the vessel | 18 | 165.85 | 168.85 | 3 | 25 | 2 m swh | [6 empty] | 150 | 150
Time required to lift nacelle | 19 | 168.85 | 169.85 | 1 | 15 | 2 m swh | [6 empty] | 50 | 50
Time required to attach the nacelle to the turbine tower | 20 | 169.85 | 175.85 | 6 | 15 | 2 m swh | [6 empty] | 300 | 300
Time required to re-equip crane | 21 | 175.85 | 176.85 | 1 | 25 | 2 m swh | [6 empty] | 50 | 50
Time required to release the turbine blade from the vessel | 22 | 176.85 | 177.85 | 1 | 25 | 2 m swh | [6 empty] | 50 | 50
Time required to lift turbine blade | 23 | 177.85 | 178.85 | 1 | 15 | 2 m swh | [6 empty] | 50 | 50
Tie required to attache the turbine blade to the nacelle | 24 | 178.85 | 182.35 | 3.5 | 15 | 2 m swh | [6 empty] | 175 | 200
Time required to release the turbine blade from the vessel | 25 | 182.35 | 183.35 | 1 | 25 | 2 m swh | [6 empty] | 50 | 50
Time required to lift turbine blade | 26 | 183.35 | 184.35 | 1 | 15 | 2 m swh | [6 empty] | 50 | 50
Tie required to attache the turbine blade to the nacelle | 27 | 184.35 | 187.85 | 3.5 | 15 | 2 m swh | [6 empty] | 175 | 200
Time required to release the turbine blade from the vessel | 28 | 187.85 | 188.85 | 1 | 25 | 2 m swh | [6 empty] | 50 | 50
Time required to lift turbine blade | 29 | 188.85 | 189.85 | 1 | 15 | 2 m swh | [6 empty] | 50 | 50
Tie required to attache the turbine blade to the nacelle | 30 | 189.85 | 193.35 | 3.5 | 15 | 2 m swh | [6 empty] | 175 | 200
Time required to jackdown | 31 | 193.35 | 194.75 | 1.4 | 25 | 2 m swh | [6 empty] | 70 | 50
Transit to port | 32 |  |  | 5 | 25 | 3 m swh |  |  |  | Transit time per trip | 5 | hr | 65 | 65 | assume 13 return trips to port (12 trips * 4 turbines plus 1 trip * 2 turbines)
[11 empty] | Total installation time (days) |  | 155.7292 | 158.3333

## Project plan - monopile install
Times for individual turbine installation processes
*Assumes 6 turbine sets transported per trip
| Relations/predecessors [row] | Start time [hours] | End time [hours] | Duration [hr] | Wind speed limit (m/s) | Wave height limit (m) | Time per monopile |  |  | Time per trip |  |  | Total installation time (unweathered) | Total installation time; 1-hour time-step (unweathered)
Mobilize vessel |  | 0 | 120 | 120 | [8 empty] | 120 | 120 | assume 1 mobilisation for vessel
Fasten monopile to vessel | 5 | 120 | 132 | 12 | 25 | 3 | Loadout time per monopile | 20 | hr | Total loadout time per trip | 120 | hr | 600 | 600 | assume all 50 monopiles loaded-out
Fasten transition piece to vessel | 6 | 132 | 140 | 8 | 25 | 3 | [6 empty] | 400 | 400
Transit to site | 7 | 140 | 145 | 5 | 25 | 3 |  |  |  | Transit time per trip | 5 | hr | 45 | 45 | assuming 9 trips: 8*6 MPs + 1*2 MPs
Position vessel onsite | 8 | 145 | 147 | 2 | 25 | 2 | Install time per monopile/transition piece pair | 17.5 | hr | Total install time per trip | 105 | hr | 100 | 100 | assume all 50 monopiles installed
ROV survey of seabed | 9 | 147 | 148 | 1 | 25 | 2 | [6 empty] | 50 | 50
Release monopile from vessel | 10 | 148 | 151 | 3 | 25 | 2 | [6 empty] | 150 | 150
Lower monopile to seabed | 11 | 151 | 152 | 1 | 15 | 2 | [6 empty] | 50 | 50
Re-equip crane with hydraulic hammer | 12 | 152 | 153 | 1 | 15 | 2 | [6 empty] | 50 | 50
Drive monopile into seabed | 13 | 153 | 154.5 | 1.5 | 15 | 2 | [6 empty] | 75 | 100
Re-equip crane | 14 | 154.5 | 155.5 | 1 | 25 | 2 | [6 empty] | 50 | 50
Release transition piece from vessel | 15 | 155.5 | 157.5 | 2 | 25 | 2 | [6 empty] | 100 | 100
Lift transition piece | 16 | 157.5 | 158.5 | 1 | 15 | 2 | [6 empty] | 50 | 50
Bolt transition piece to monopile | 17 | 158.5 | 162.5 | 4 | 15 | 2 | [6 empty] | 200 | 200
Transit to site | 18 |  |  | 5 | 25 | 3 |  |  |  | Transit time per trip | 5 | hr | 45 | 45 | assuming 9 return trips
[11 empty] | Total installation time (days) |  | 86.875 | 87.9167

## Project plan - array cable inst
Times for array cable installation processes
* Assumes all cable carried/laid/buried in a single trip
| Relations/predecessors [row] | Start time [hours] | End time [hours] | Duration [hr] | Wind speed limit (m/s) | Wave height limit (m) | Time per turbine |  |  | Total project time |  |  | Total installation time (unweathered) | Total installation time; 1-hour time-step (unweathered)
Mobilize vessel |  | 0 | 120 | 120 | [8 empty] | 120 | 120 | assume 1 mobilisation for vessel
Load cable at port | 5 | 120 | 126 | 6 | 25 | 2 | [6 empty] | 6 | 6 | assume a single load-out of cable
Transit to site | 6 | 126 | 132.2 | 6.2 | 25 | 2 | [6 empty] | 6.2 | 6 | assume a single trip to site
Position onsite | 7 | 132.2 | 134.2 | 2 | 25 | 2 | Cable prep and lay per turbine | 24.9 | hr | Total time | 1245 | hr | 100 | 100 | assume all 50 cables installed
Prepare cable | 8 | 134.2 | 135.2 | 1 | 25 | 2 | [6 empty] | 50 | 50
Pull in cable at turbine | 9 | 135.2 | 140.7 | 5.5 | 25 | 2 | [6 empty] | 275 | 300
Terminate cable | 10 | 140.7 | 146.2 | 5.5 | 25 | 2 | [6 empty] | 275 | 300
Lower cable to seafloor | 11 | 146.2 | 147.2 | 1 | 25 | 2 | [6 empty] | 50 | 50
Lay/bury cable to next turbine in string | 12 | 147.2 | 157.1 | 9.9 | 25 | 2 | [6 empty] | 495 | 500
Transit to port |  |  |  | 6.2 | 25 | 2 | [6 empty] | 6.2 | 6 | assume a single return trip to port
[11 empty] | Total installation time (days) |  | 57.6417 | 59.9167

## Project plan - export cable ins
Times for export cable installation processes
* Assumes all cable carried/laid/buried in a single trip
| Relations/predecessors [row] | Start time [hours] | End time [hours] | Duration [hr] | Wind speed limit (m/s) | Wave height limit (m) | Total time per cable |  |  | Total project time |  |  | Total installation time (unweathered) | Total installation time; 1-hour time-step (unweathered)
Mobilize vessel |  | 0 | 168 | 168 | [10 empty] | assume 1 mobilisation for vessel
Load cable at port | 5 | 168 | 174 | 6 | 25 | 2 | [8 empty] | assume a single load-out of cable
Position at landfall | 7 | 174 | 176 | 2 | 25 | 2 | Cable prep and lay total | #REF! | hr | Total time | #REF! | hr |  |  | assume all 50 cables installed
Prepare cable | 8 | 176 | 177 | 1 | 25 | 2
Pull in cable | 9 | 177 | 182.5 | 5.5 | 25 | 2
Lower cable to seafloor | 11 | 182.5 | 183.5 | 1 | 25 | 2
Lay/bury cable to offshore substation | 12 | 183.5 | #REF! | #REF! | 25 | 2
Terminate cable | 10 | 182.5 | 188 | 5.5 | 25 | 2
Transit to port |  |  |  | 6.2 | 25 | 2 | [8 empty] | assume a single return trip to port
Total installation time (days)

## Project plan - OSS install
Times for substation installation process
*Assumes two OSS at site
| Relations/predecessors [row] | Start time [hours] | End time [hours] | Duration [hr] | Wind speed limit (m/s) | Wave height limit (m) | Time per substation |  |  | Time per trip |  |  | Total installation time (unweathered)
[13 empty] | 0 | assume 1 mobilisation for vessel
Assume vessel mobilisation and load out carried out for foundation installation | [12 empty] | 0 | assume all 50 monopiles loaded-out
Fasten monopile |  | 0 | 12 | 12 | 25 | 3
Fasten topside | 8 | 12 | 24 | 12 | 25 | 3 | [6 empty] | 600
Transit to site | 7 | 24 | 29 | 5 | 25 | 2 |  |  |  | Transit time per trip | 5 | hr | 5 | assuming 9 trips: 8*6 MPs + 1*2 MPs
Position vessel onsite | 8 | 29 | 31 | 2 | 25 | 2 | Install time per substation | 29.5 | hr | Total install time per trip | 29.5 | hr | 2 | assume all 50 monopiles installed
ROV survey of seabed | 9 | 31 | 32 | 1 | 25 | 2 | [6 empty] | 1
Release monopile from vessel | 10 | 32 | 35 | 3 | 25 | 2 | [6 empty] | 3
Lower monopile to seabed | 11 | 35 | 36 | 1 | 15 | 2 | [6 empty] | 1
Re-equip crane with hydraulic hammer | 12 | 36 | 37 | 1 | 15 | 2 | [6 empty] | 1
Drive monopile into seabed | 13 | 37 | 38.5 | 1.5 | 15 | 2 | [6 empty] | 1.5
Re-equip crane | 14 | 38.5 | 39.5 | 1 | 25 | 2 | [6 empty] | 1
Release transition piece from vessel | 15 | 39.5 | 41.5 | 2 | 25 | 2 | [6 empty] | 2
Lift transition piece | 16 | 41.5 | 42.5 | 1 | 15 | 2 | [6 empty] | 1
Bolt transition piece to monopile | 17 | 42.5 | 46.5 | 4 | 15 | 2 | [6 empty] | 4
Lift substation topside | 18 | 46.5 | 54.5 | 8 | 15 | 2
Bolt topside to transition piece | 19 | 54.5 | 58.5 | 4 | 15 | 2
Transit to site | 18 |  |  | 5 | 25 | 2 |  |  |  | Transit time per trip | 5 | hr | 5 | assuming 9 return trips
[11 empty] | Total installation time (days) |  | 26.1458

## Project plan - scour protection
Times for scour protection installation process
| Relations/predecessors [row] | Start time [hours] | End time [hours] | Duration [hr] | Wind speed limit (m/s) | Wave height limit (m) | Time per substructure |  |  | Time per trip |  |  | Total installation time (unweathered)
Mobilize vessel |  | 0 | 168 | 168 | [8 empty] | 168 | assume 1 mobilisation for vessel
Load rocks at port | 5 | 168 | 172 | 4 | 25 | 3 |  |  |  | Transit time per trip | 40 | hr | 4 | assuming 25 trips
Transit to site | 6 | 172 | 192 | 20 | 20 | 2 | Scour protection time per substructure | 10.25 | hr | Total install time per trip | 20.25 | hr | 20
Dump rocks at substructure |  | 192 | 202 | 10 | 20 | 2 | [6 empty] | 10
Transit to next turbine |  | 202 | 202.25 | 0.25 | 20 | 2 | [6 empty] | 0.25
Dump rocks at substructure |  | 202.25 | 212.25 | 10 | 20 | 2 | [6 empty] | 10
Transit to port |  | 212.25 | 232.25 | 20 | 20 | 2 | [6 empty] | 20
[11 empty] | Total installation time (days) |  | 9.6771